## Measurements overview
Measured parameter | Additional parameters of interest
Input Step Response
Output ripple at different loads
Output step response | Overshoot, undershoot, recovery time
Safety parameters | Voltage and current limits, battery charge termination voltage
Validate, that the actual MPP is found!

## Efficiency
Efficiency vs Ouput Power and Input Voltage
[8 empty] | Uin | Avg Efficiency
Efficiency vs Ouput Power at Uin = 16V | [7 empty] | 16 | 0.92184
Wirkungsgrad vs Ausgangsleistung bei Uin = 16V | [5 empty] | Average Efficiency | 0.92184 | 26 | 0.92748
Uin | Iin | Pin | Uout | Iout | Pout | Efficiency |  | 36 | 0.91852
16 | 0.032 | 0.512 | 48 | 0 | 0
16 | 0.5 | 8 | 48.1 | 0.153 | 7.3593 | 0.91991
16 | 0.9 | 14.4 | 46.5 | 0.282 | 13.113 | 0.91062
16 | 1.5 | 24 | 48.7 | 0.462 | 22.4994 | 0.93748
16 | 2.19 | 35.04 | 48.8 | 0.673 | 32.8424 | 0.93728
16 | 2.86 | 45.76 | 48.8 | 0.872 | 42.5536 | 0.92993
16 | 3.54 | 56.64 | 48.8 | 1.07 | 52.216 | 0.92189
16 | 4.3 | 68.8 | 49 | 1.296 | 63.504 | 0.92302
16 | 4.95 | 79.2 | 48.9 | 1.48 | 72.372 | 0.91379
16 | 5.7 | 91.2 | 49 | 1.68 | 82.32 | 0.90263
16 |  | 0 |  |  | 0 | #DIV/0!
16 |  | 0 |  |  | 0 | #DIV/0!
16 |  | 0 |  |  | 0 | #DIV/0!
Efficiency vs Ouput Power at Uin = 26V
Wirkungsgrad vs Ausgangsleistung bei Uin = 26V | [5 empty] | Average Efficiency | 0.92748
Uin | Iin | Pin | Uout | Iout | Pout | Efficiency
26 | 0.038 | 0.988 | 48 | 0 | 0
26 | 0.2 | 5.2 | 30 | 0.14 | 4.2 | 0.80769
26 | 0.54 | 14.04 | 49.6 | 0.26 | 12.896 | 0.91852
26 | 0.85 | 22.1 | 49.5 | 0.42 | 20.79 | 0.94072
26 | 1.35 | 35.1 | 49.2 | 0.678 | 33.3576 | 0.95036
26 | 1.73 | 44.98 | 49.2 | 0.857 | 42.1644 | 0.9374
26 | 2.18 | 56.68 | 49.3 | 1.09 | 53.737 | 0.94808
26 | 2.47 | 64.22 | 49.5 | 1.23 | 60.885 | 0.94807
26 | 2.88 | 74.88 | 49.6 | 1.43 | 70.928 | 0.94722
26 | 3.4 | 88.4 | 49.2 | 1.677 | 82.5084 | 0.93335
26 | 3.8 | 98.8 | 49.2 | 1.89 | 92.988 | 0.94117
26 | 4.2 | 109.2 | 49.2 | 2.07 | 101.844 | 0.93264
26 | 4.82 | 125.32 | 49.3 | 2.35 | 115.855 | 0.92447
Efficiency vs Ouput Power at Uin = 36V
Wirkungsgrad vs Ausgangsleistung bei Uin = 36V | [5 empty] | Average Efficiency | 0.91852
Uin | Iin | Pin | Uout | Iout | Pout | Efficiency
36 | 0.025 | 0.9 | 48 | 0 | 0
36 | 0.175 | 6.3 | 48 | 0.103 | 4.944 | 0.78476
36 | 0.268 | 9.648 | 49.6 | 0.167 | 8.2832 | 0.85854
36 | 0.36 | 12.96 | 48.6 | 0.234 | 11.3724 | 0.8775
36 | 0.52 | 18.72 | 49.2 | 0.348 | 17.1216 | 0.91462
36 | 1.035 | 37.26 | 49.5 | 0.7 | 34.65 | 0.92995
36 | 1.3 | 46.8 | 49.5 | 0.902 | 44.649 | 0.95404
36 | 1.51 | 54.36 | 49.5 | 1.05 | 51.975 | 0.95613
36 | 1.83 | 65.88 | 49.6 | 1.26 | 62.496 | 0.94863
36 | 2.1 | 75.6 | 49.5 | 1.46 | 72.27 | 0.95595
36 | 2.4 | 86.4 | 49.5 | 1.66 | 82.17 | 0.95104
36 | 2.91 | 104.76 | 49.6 | 2 | 99.2 | 0.94693
36 | 3.4 | 122.4 | 49.6 | 2.33 | 115.568 | 0.94418

## Ouput Step Response
Measurements without series resistor on input
OutputStep
Vin | 36V
Vout | 50V
Pout |  | FileName | Note | Output gets stuck but recovers after some time | ONLY with slow algorithm timing
20W | 1 | OutputStepVin =36VVout =50VPout=20W
40W | 2 | OutputStepVin =36VVout =50VPout=40W
60W | 3 | OutputStepVin =36VVout =50VPout=60W
80W | 4 | OutputStepVin =36VVout =50VPout=80W
100W | 5 | OutputStepVin =36VVout =50VPout=100W

## Input Step Response
Measurements without series resistor on input
InputStepResponse
Vout | 50V
StepFrom | StepTo | Pout |  | FileName
16V | 36V | 0 | 1 | InputStepResponseStepFrom16VStepTo36VPout=0W
16V | 36V | 20 | 2 | InputStepResponseStepFrom16VStepTo36VPout=20W
16V | 36V | 40 | 3 | InputStepResponseStepFrom16VStepTo36VPout=40W
16V | 36V | 60 | 4 | InputStepResponseStepFrom16VStepTo36VPout=60W
36V | 16V | 0 | 5 | InputStepResponseStepFrom36VStepTo16VPout=0W
36V | 16V | 20 | 6 | InputStepResponseStepFrom36VStepTo16VPout=20W
36V | 16V | 40 | 7 | InputStepResponseStepFrom36VStepTo16VPout=40W
36V | 16V | 60 | 8 | InputStepResponseStepFrom36VStepTo16VPout=60W

## Ouput Ripple
Measurements without series resistor on input
OutputRipple
Vout | 50V
Vin | Pout |  | FileName
36V | 0W | 1 | OutputRippleVin=36VPout=0W
36V | 10W | 2 | OutputRippleVin=36VPout=10W
36V | 20W | 3 | OutputRippleVin=36VPout=20W
36V | 40W | 4 | OutputRippleVin=36VPout=40W
36V | 60W | 5 | OutputRippleVin=36VPout=60W
36V | 80W | 6 | OutputRippleVin=36VPout=80W
36V | 100W | 7 | OutputRippleVin=36VPout=100W